## BoQ1 (hidden)
Item Rate BoQ
BoQ_Ver3.1 | Item Rate | Normal | INR Only | INR
Select, Excess (+), Less (-) |  | Less (-)
Tender Inviting Authority: Superintending Engineer, IISER Thiruvananthapuram
Name of Work: Electrical works for landscaping area in students park at IISER TVM campus, Thiruvananthapuram
Contract No: 04712778039/8036
Name of the Bidder/ Bidding Firm / Company :
PRICE SCHEDULE (This BOQ template must not be modified/replaced by the bidder and the same should be uploaded after filling the relevant columns, else the bidder is liable to be rejected for this tender. Bidders are allowed to enter the Bidder Name and Values only )
NUMBER # | TEXT # | TEXT # | NUMBER # | TEXT # | NUMBER | NUMBER | TEXT | TEXT # | NUMBER # | TEXT# | TEXT # | NUMBER # | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER # | NUMBER # | TEXT | TEXT | NUMBER # | NUMBER # | DATE | NUMBER # | NUMBER # | TEXT #
Sl. No. | Item Description | Item Code / Make | Quantity | Units | Estimated Rate in Rs. P |  |  | Addition / Deduction | Addition / Deduction Values | Currency Convertion against each Item | Quoted Currency in INR / Other Currency | Rate in Figures to be entered by the bidder in Rs. p | Excise Duty | VAT | Freight Charges ( Unloading & Stacking) | Any Other Taxes/Duties/Levies |  |  | Other Taxes 2 | IIIrd Party i.e DGS&D / RITES etc Inspection Charges @0.34%+Service Tax | Less for Cenvat Credit,if any respect of Supplies Under full Excise Duty Category | [30 empty] | TOTAL AMOUNT With Taxes Rs. P | TOTAL AMOUNT | TOTAL AMOUNT In Words
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 7 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | 40 | 41 | 42 | 43 | 44 | 45 | 46 | 47 | 48 | 49 | 50 | 51 | 52 | 8 | 9 | 10
1 | Supply, installation, testing and commissioning of Solar LED Street light with in built PIR Sensor , power up to 25W LED All-in-One Solar Streetlight with System efficeny not less than 120 lm/W. System lumen o/p not less than 3000 lumens. 40Wp High Efficiency Monocrystalline Silicon Panel. suitable Ah LiFePO4 Battery with higher life of >2000 cycles. At Full Power ≥10 Hrs autonomy and at Saving mode ≥30Hrs autonomy. Automatic Dusk to Dawn feature. Integral PIR sensor for motion detection. MPPT charge controller with 90-96% efficiency. System voltage: 12V. LEDs used in the product shall comply with EN 62471 for Photo-biological safety and certificate for the same from manufacturer shall be provided. Luminaire shall be with IP65 protection. The LED shall be compliant with LM80-08 standard with L70 life of 50000 Hrs tested at maximum current (Complete LM 80 test report for LED should be submitted for 10000 hrs of testing). The LEDs used should be with CCT of 5700 - 6500 K and CRI >70 with 3.5metre to 4 metre high decorative conical pole/GI Octogonal pole prefabricated with suitable size with foundation bolt & nuts ,all accesories complete as required including necessary foundation and pole earthing.( Solar street light-(Wipro/bajaj/philips/crompton or Equivalent ). conical Pole-Klite or equivalent, Octogonal pole-Crompton/Bajaj or Equivalent. Warranty-(3 years onsite full warranty and 2 years service warranty ) Total - Min. 5 years warranty for Led street light Note: Approval shall be taken from EIC before supply of Pole and LED Solar street light. |  | 10 | Each | 51956 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 0 | 0 | INR Zero Only | 1 | Supply, installation, testing and commissioning of Solar LED Street light with in built PIR Sensor , power up to 25W LED All-in-One Solar Streetlight with System efficeny not less than 120 lm/W. System lumen o/p not less than 3000 lumens. 40Wp High Efficiency Monocrystalline Silicon Panel. suitable Ah LiFePO4 Battery with higher life of >2000 cycles. At Full Power ≥10 Hrs autonomy and at Saving mode ≥30Hrs autonomy. Automatic Dusk to Dawn feature. Integral PIR sensor for motion detection. MPPT charge controller with 90-96% efficiency. System voltage: 12V. LEDs used in the product shall comply with EN 62471 for Photo-biological safety and certificate for the same from manufacturer shall be provided. Luminaire shall be with IP65 protection. The LED shall be compliant with LM80-08 standard with L70 life of 50000 Hrs tested at maximum current (Complete LM 80 test report for LED should be submitted for 10000 hrs of testing). The LEDs used should be with CCT of 5700 - 6500 K and CRI >70 with 3.5metre to 4 metre high decorative conical pole/GI Octogonal pole prefabricated with suitable size with foundation bolt & nuts ,all accesories complete as required including necessary foundation and pole earthing.( Solar street light-(Wipro/bajaj/philips/crompton or Equivalent ). conical Pole-Klite or equivalent, Octogonal pole-Crompton/Bajaj or Equivalent. Warranty-(3 years onsite full warranty and 2 years service warranty ) Total - Min. 5 years warranty for Led street light Note: Approval shall be taken from EIC before supply of Pole and LED Solar street light. | 10 | Each
2 | Supply, installation, testing and commissioning of decorative solar post top lantern 3000 to 4000K with in built LED fixture up to 15W , solar panel -suitable rating of monocrystalline x 2 , Inbuilt battery of suitable Ah, with Suitable charging time, Backup time- 12 to 14 hrs with 2.5metre to 3metre high decorative conical pole prefabricated with suitable size Tightness: IP 65 with foundation bolt & nuts ,all accesories complete as required including necessary foundation and pole earthing .( Luker (Model-LPTSOL2600 )or Equivalent ). Luminare data Operation-Automatic On/off using LDR Sensor LED Life greater than 30,000, Lumen output-1000 lumens Warranty-5 years on site Note: Approval shall be taken from EIC before supply of decorative solar post top lantern |  | 4 | Each | 25844 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 0 | 0 | INR Zero Only | 2 | Supply, installation, testing and commissioning of decorative solar post top lantern 3000 to 4000K with in built LED fixture up to 15W , solar panel -suitable rating of monocrystalline x 2 , Inbuilt battery of suitable Ah, with Suitable charging time, Backup time- 12 to 14 hrs with 2.5metre to 3metre high decorative conical pole prefabricated with suitable size Tightness: IP 65 with foundation bolt & nuts ,all accesories complete as required including necessary foundation and pole earthing .( Luker (Model-LPTSOL2600 )or Equivalent ). Luminare data Operation-Automatic On/off using LDR Sensor LED Life greater than 30,000, Lumen output-1000 lumens Warranty-5 years on site Note: Approval shall be taken from EIC before supply of decorative solar post top lantern | 4 | Each
3 | Supply, installation, testing and commissioning of outdoor Bush light for illumination of tree (with all accesories for fixing) up to 12W, High efficient LED with Aluminium housing with clear toughened glass cover.CRI>70, IP65, CCT - 2700K, Ambient temp-0 to 45 DegC, Driver efficiency>85%,THD<25%, Powerfactor>0.95, Surge protection-2 kV, Multistage Isolated Constant Current-Constant Voltage driver and Safety Extra Low Voltage Safe level<60V DC as per IEC standard. Luminaire lumen ≥ 600 lumens (75 lm/W) Make: Wipro/Klite/Philips or Equivalent. Warranty: 3years Note: Approval shall be taken from EIC before supply of Bush light. |  | 2 | Each | 4581 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 0 | 0 | INR Zero Only | 3 | Supply, installation, testing and commissioning of outdoor Bush light for illumination of tree (with all accesories for fixing) up to 12W, High efficient LED with Aluminium housing with clear toughened glass cover.CRI>70, IP65, CCT - 2700K, Ambient temp-0 to 45 DegC, Driver efficiency>85%,THD<25%, Powerfactor>0.95, Surge protection-2 kV, Multistage Isolated Constant Current-Constant Voltage driver and Safety Extra Low Voltage Safe level<60V DC as per IEC standard. Luminaire lumen ≥ 600 lumens (75 lm/W) Make: Wipro/Klite/Philips or Equivalent. Warranty: 3years Note: Approval shall be taken from EIC before supply of Bush light. | 2 | Each
4 | Supply of following sizes 1.1 KV XLPE insulated, FRLS Al. armoured Conductor, PVC inner sheathed, overall PVC sheathed cable in conformity to the technical specification and as per latest IS - codes. | [53 empty] | 4 | Supply of following sizes 1.1 KV XLPE insulated, FRLS Al. armoured Conductor, PVC inner sheathed, overall PVC sheathed cable in conformity to the technical specification and as per latest IS - codes.
4.1 | 3 x 4 Sqmm |  | 125 | Metre | 92 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 0 | 0 | INR Zero Only | 4.1 | 3 x 4 Sqmm | 125 | Metre
5 | Laying of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of following size direct in ground/on wall surface/ existing Trench/ HUME/ METAL pipe/DWC pipe etc as required. | [53 empty] | 5 | Laying of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of following size direct in ground/on wall surface/ existing Trench/ HUME/ METAL pipe/DWC pipe etc as required.
5.1 | upto 35 Sqmm |  | 125 | Metre | 205 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 0 | 0 | INR Zero Only | 5.1 | upto 35 Sqmm | 125 | Metre
6 | Supply and making end termination with brass compression gland with gland earthing and aluminium lugs for following size of PVC insulated and PVC sheathed /XLPE Al. conductor cable of 1.1 KV grade as required. | [53 empty] | 6 | Supply and making end termination with brass compression gland with gland earthing and aluminium lugs for following size of PVC insulated and PVC sheathed /XLPE Al. conductor cable of 1.1 KV grade as required.
6.1 | 3 x 4 Sqmm |  | 6 | Each | 267 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 0 | 0 | INR Zero Only | 6.1 | 3 x 4 Sqmm | 6 | Each
7 | Supply , installation,Testing &Commissioning of weather proof thermoplastic enclosure complete with Two Nos. of 6A SP MCB ,DIN rail, Suitable N.L and connector etc.on wall or fabricated MS channel as required. |  | 1 | Each | 1566 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 0 | 0 | INR Zero Only | 7 | Supply , installation,Testing &Commissioning of weather proof thermoplastic enclosure complete with Two Nos. of 6A SP MCB ,DIN rail, Suitable N.L and connector etc.on wall or fabricated MS channel as required. | 1 | Each
Total in Figures | [51 empty] | 0 | 0 | INR Zero Only
Quoted Rate in Figures |  |  |  | Select | [47 empty] | 0 | 0 | Zero Only
Quoted Rate in Words |  | INR Zero Only

## Macros
Please Enable Macros to View BoQ information