## Sheet1
Item Rate BoQ
BoQ_Ver3.1 | Item Rate | Normal | INR Only | INR
Select, Excess (+), Less (-) |  | Less (-)
Tender Inviting Authority: Project Engineer cum Estate Officer(I/C), IISER Thiruvananthapuram
Name of Work: Annual Maintenance Contract for Fire Fighting systems, Fire alarm and Public Addressing systems, refilling of fire extinguishers installed in IISER campus, Thiruvananthapuram
Contract No: 04712778039/8036
Name of the Bidder/ Bidding Firm / Company :
PRICE SCHEDULE (This BOQ template must not be modified/replaced by the bidder and the same should be uploaded after filling the relevant columns, else the bidder is liable to be rejected for this tender. Bidders are allowed to enter the Bidder Name and Values only )
NUMBER # | TEXT # | TEXT # | NUMBER # | TEXT # | NUMBER | NUMBER | TEXT | TEXT # | NUMBER # | TEXT# | TEXT # | NUMBER # | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER # | NUMBER # | TEXT | TEXT | NUMBER # | NUMBER # | DATE | NUMBER # | NUMBER # | TEXT #
Sl. No. | Item Description | Item Code / Make | Quantity | Units | Estimated Rate in Rs. P |  |  | Addition / Deduction | Addition / Deduction Values | Currency Convertion against each Item | Quoted Currency in INR / Other Currency | Rate in Figures to be entered by the bidder in Rs. p | Excise Duty | VAT | Freight Charges ( Unloading & Stacking) | Any Other Taxes/Duties/Levies |  |  | Other Taxes 2 | IIIrd Party i.e DGS&D / RITES etc Inspection Charges @0.34%+Service Tax | Less for Cenvat Credit,if any respect of Supplies Under full Excise Duty Category | [30 empty] | TOTAL AMOUNT With Taxes Rs. P | TOTAL AMOUNT | TOTAL AMOUNT In Words
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 7 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | 40 | 41 | 42 | 43 | 44 | 45 | 46 | 47 | 48 | 49 | 50 | 51 | 52 | 8 | 9 | 10
1 | Routine operation and maintenance of Fire Fighting equipments, Internal & External Fire Hydrant,First Aid hose reel drums, Fire Extinguishers,RRL Hose, FBC, all type Valves including repairing of defective parts of above installations and cleaning, Regular Testing, including connection and interconnections etc. as reqd on all working days including sunday and holiday as per duty chart ( Manpower to be deployed as given below ) reqd as per the terms and conditions. Details of Fire hydrant equipments attached seperatly as Annexure-1 Fireman ( For Regular Testing of system and Fire Incidents ) = 1 No. Duty time: 9.00am to 5.30pm on all days |  | 12 | Month | 32154 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 0 | 0 | #NAME? | 1 | Routine operation and maintenance of Fire Fighting equipments, Internal & External Fire Hydrant,First Aid hose reel drums, Fire Extinguishers,RRL Hose, FBC, all type Valves including repairing of defective parts of above installations and cleaning, Regular Testing, including connection and interconnections etc. as reqd on all working days including sunday and holiday as per duty chart ( Manpower to be deployed as given below ) reqd as per the terms and conditions. Details of Fire hydrant equipments attached seperatly as Annexure-1 Fireman ( For Regular Testing of system and Fire Incidents ) = 1 No. Duty time: 9.00am to 5.30pm on all days | 12 | Month
2 | Routine, operation and maintenance of Fire Alarm equipments and PA System, Fire control panels,Photo / Thermal Detectors, Relay / Control Module,Fault Isolators, Manual Call Points, Response Indicators, AC duct Detectors and Hooters including repairing of defective parts of above installations, addressing of the FACP and cleaning including connection and interconnection etc.required as per the terms and conditions. Details of Fire alarm equipments attached seperatly as Annexure-2 |  | 4 | Job | 30827 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 0 | 0 | #NAME? | 2 | Routine, operation and maintenance of Fire Alarm equipments and PA System, Fire control panels,Photo / Thermal Detectors, Relay / Control Module,Fault Isolators, Manual Call Points, Response Indicators, AC duct Detectors and Hooters including repairing of defective parts of above installations, addressing of the FACP and cleaning including connection and interconnection etc.required as per the terms and conditions. Details of Fire alarm equipments attached seperatly as Annexure-2 | 4 | Job
3 | Servicing and Refilling of stored pressure Dry Chemical Powder type (ABC Stored Pressure Type) fire extinguishers with Mono Ammonium Phosphate based dry chemical powder (MAP min 90%) & Hygroscopicity less than 1.5% confirming to IS: 14609, IS 15683:2006 capable of fighting class A, B, C types of fires with Dry Nitrogen based propellant 15Kg/Cm2 as required. If necessary as per the site condition the fire extinguisher shall be provided with accessories/spares like Pressure Gauge, Safety Pin, Bracket, Valve assembly, Horn & Hose etc. complete for safe operation as per IS standards, Instruction sticker, scratching off rusts and repainting with suitable shade confirming to IS: 2932) and fixing on wall and transportation complete in all aspects as per IS: 2190 as directed by EIC. (The operating temperature range, Net weight, the effective discharge time & throw, Expiry date shall be clearly mentioned in the extinguisher.) | [6 empty] | Excess(+) | 1 | Full Conversion | INR | [43 empty] | 3 | Servicing and Refilling of stored pressure Dry Chemical Powder type (ABC Stored Pressure Type) fire extinguishers with Mono Ammonium Phosphate based dry chemical powder (MAP min 90%) & Hygroscopicity less than 1.5% confirming to IS: 14609, IS 15683:2006 capable of fighting class A, B, C types of fires with Dry Nitrogen based propellant 15Kg/Cm2 as required. If necessary as per the site condition the fire extinguisher shall be provided with accessories/spares like Pressure Gauge, Safety Pin, Bracket, Valve assembly, Horn & Hose etc. complete for safe operation as per IS standards, Instruction sticker, scratching off rusts and repainting with suitable shade confirming to IS: 2932) and fixing on wall and transportation complete in all aspects as per IS: 2190 as directed by EIC. (The operating temperature range, Net weight, the effective discharge time & throw, Expiry date shall be clearly mentioned in the extinguisher.)
3.1 | 4kg (ABC) |  | 323 | Nos | 531 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 0 | 0 | #NAME? | 3.1 | 4kg (ABC) | 323 | Nos
3.2 | 6kg (ABC) |  | 89 | Nos | 767 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 0 | 0 | #NAME? | 3.2 | 6kg (ABC) | 89 | Nos
3.3 | 9kg (ABC) |  | 8 | Nos | 944 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 0 | 0 | #NAME? | 3.3 | 9kg (ABC) | 8 | Nos
3.4 | 50kg (ABC) |  | 3 | Nos | 4720 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 0 | 0 | #NAME? | 3.4 | 50kg (ABC) | 3 | Nos
3.5 | 10 kg (ABC) with sprinkler head modular automatic |  | 11 | Nos | 1298 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 0 | 0 | #NAME? | 3.5 | 10 kg (ABC) with sprinkler head modular automatic | 11 | Nos
4 | Servicing and Refilling of stored pressure Dry Chemical Powder type fire extinguishers with Sodium-Bi-Carbonate (SBC) suitable for B and C Class Fire (as per IS:4308 latest revision, IS:15683),with gas cartridge having Propellant of 120 grams CO2 stored as per IS: 4947, having a Minimum Effective Discharge Time of 8seconds. All the extinguisher shall be Hydraulic Pressure Testing as per IS: 2190. If necessary as per the site condition the fire extinguisher shall be provided with accessories/spares like Pressure Gauge, Safety Pin, Bracket, Valve assembly, Horn & Hose etc. complete for safe operation as per IS standards, repainting with suitable shade confirming to IS: 2932, Labour cost, transportation complete as required including all the taxes complete in all aspects as directed by EIC. (The operating temperature range, Net weight, the effective discharge time & throw shall be clearly mentioned in the extinguisher.) | [6 empty] | Excess(+) | 1 | Full Conversion | INR | [43 empty] | 4 | Servicing and Refilling of stored pressure Dry Chemical Powder type fire extinguishers with Sodium-Bi-Carbonate (SBC) suitable for B and C Class Fire (as per IS:4308 latest revision, IS:15683),with gas cartridge having Propellant of 120 grams CO2 stored as per IS: 4947, having a Minimum Effective Discharge Time of 8seconds. All the extinguisher shall be Hydraulic Pressure Testing as per IS: 2190. If necessary as per the site condition the fire extinguisher shall be provided with accessories/spares like Pressure Gauge, Safety Pin, Bracket, Valve assembly, Horn & Hose etc. complete for safe operation as per IS standards, repainting with suitable shade confirming to IS: 2932, Labour cost, transportation complete as required including all the taxes complete in all aspects as directed by EIC. (The operating temperature range, Net weight, the effective discharge time & throw shall be clearly mentioned in the extinguisher.)
4.1 | 6 kg ( BC Type ) |  | 11 | Nos | 649 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 0 | 0 | #NAME? | 4.1 | 6 kg ( BC Type ) | 11 | Nos
5 | Servicing and Refilling of existing CO2 based Fire Extinguisher of following capacity at various location at IISER Campus with carbon dioxide gas conforming to IS:15222, IS:2190,IS: 2878,IS:15683 if necessary It shall have anti corrosive treatment as per IS 3203. The extinguisher shall be clearly and permanently marked in accordance with IS: 940(latest amendment), repainting with suitable shade confirming to IS: 2932.etc complete in all aspects as directed by EIC. (The operating temperature range, Net weight, the effective discharge time & throw, Expiry date shall be clearly mentioned in the extinguisher.) | [6 empty] | Excess(+) | 1 | Full Conversion | INR | [43 empty] | 5 | Servicing and Refilling of existing CO2 based Fire Extinguisher of following capacity at various location at IISER Campus with carbon dioxide gas conforming to IS:15222, IS:2190,IS: 2878,IS:15683 if necessary It shall have anti corrosive treatment as per IS 3203. The extinguisher shall be clearly and permanently marked in accordance with IS: 940(latest amendment), repainting with suitable shade confirming to IS: 2932.etc complete in all aspects as directed by EIC. (The operating temperature range, Net weight, the effective discharge time & throw, Expiry date shall be clearly mentioned in the extinguisher.)
5.1 | 2 Kg |  | 8 | Nos | 413 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 0 | 0 | #NAME? | 5.1 | 2 Kg | 8 | Nos
5.2 | 4.5 Kg |  | 24 | Nos | 590 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 0 | 0 | #NAME? | 5.2 | 4.5 Kg | 24 | Nos
5.3 | 22.5 kg |  | 4 | Nos | 2950 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 0 | 0 | #NAME? | 5.3 | 22.5 kg | 4 | Nos
6 | Servicing and Refilling of existing stored pressure Fire Extinguisher of Water (3A type fire) /with Gas cartridge having Propellant of 120 grams CO2 stored according to IS 4947, IS: 15683, it shall have a minimum effective discharge Time 13 Seconds and shall be moisture free and 99% pure and shall conform to the requirement of IS 15222. If necessary it shall have an Epoxy powder coating of 50 microns thickness shall be applied on external surface of the body as per IS 3203 . The extinguisher shall be clearly and permanently marked in accordance with IS: 940 (latest amendment).etc. complete in all aspects as directed by EIC. (The operating temperature range, Net weight, the effective discharge time & throw, Expiry date shall be clearly mentioned in the extinguisher.) | [6 empty] | Excess(+) | 1 | Full Conversion | INR | [43 empty] | 6 | Servicing and Refilling of existing stored pressure Fire Extinguisher of Water (3A type fire) /with Gas cartridge having Propellant of 120 grams CO2 stored according to IS 4947, IS: 15683, it shall have a minimum effective discharge Time 13 Seconds and shall be moisture free and 99% pure and shall conform to the requirement of IS 15222. If necessary it shall have an Epoxy powder coating of 50 microns thickness shall be applied on external surface of the body as per IS 3203 . The extinguisher shall be clearly and permanently marked in accordance with IS: 940 (latest amendment).etc. complete in all aspects as directed by EIC. (The operating temperature range, Net weight, the effective discharge time & throw, Expiry date shall be clearly mentioned in the extinguisher.)
6.1 | 9 liter |  | 333 | Nos | 354 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 0 | 0 | #NAME? | 6.1 | 9 liter | 333 | Nos
7 | Servicing and Refilling of Fire Extinguisher of Foam (AFFF-6% for A and B Class Fire), type as per the relevent IS standard. If necessary it shall have an Epoxy powder coating of 50 microns thickness shall be applied on external surface of the body as per IS 3203 . The extinguisher shall be clearly and permanently marked in accordance with IS: 940 (latest amendment).etc. complete in all aspects as directed by EIC. (The operating temperature range, Net weight, the effective discharge time & throw, Expiry date shall be clearly mentioned in the extinguisher.) | [6 empty] | Excess(+) | 1 | Full Conversion | INR | [43 empty] | 7 | Servicing and Refilling of Fire Extinguisher of Foam (AFFF-6% for A and B Class Fire), type as per the relevent IS standard. If necessary it shall have an Epoxy powder coating of 50 microns thickness shall be applied on external surface of the body as per IS 3203 . The extinguisher shall be clearly and permanently marked in accordance with IS: 940 (latest amendment).etc. complete in all aspects as directed by EIC. (The operating temperature range, Net weight, the effective discharge time & throw, Expiry date shall be clearly mentioned in the extinguisher.)
7.1 | 9 liter |  | 6 | Nos | 472 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 0 | 0 | #NAME? | 7.1 | 9 liter | 6 | Nos
Total in Figures | [51 empty] | 0 | 0 | #NAME?
Quoted Rate in Figures |  |  |  | Select | [47 empty] | 0 | 0 | #NAME?
Quoted Rate in Words |  | #NAME?